Copyright 2015 by The American Institute of Architects (AIA)

Exclusively published and distributed by AVITRU, LLC for the AIA

This Product MasterSpec Section is licensed by AVITRU, LLC to Armacell LLC ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Avitru or The American Institute of Architects (AIA). Neither AIA nor Avitru are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Armacell LLC, 55 Vilcom Center Drive, Suite 200, Chapel Hill, NC 27514; Phone: (984) 364-7433; Website: www.armacell.us; Email: thomas.j.mackinnon@armacell.com.

For information about MasterSpec, contact Avitru at (800) 424-5080 or visit avitru.com.

SECTION 230719 - HVAC PIPING INSULATION

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section includes insulating the following HVAC piping systems:

The list below matches the various piping systems in the schedule articles. Coordinate the revision of list with "Piping Insulation Schedule, General," "Indoor Piping Insulation Schedule," "Outdoor, Aboveground Piping Insulation Schedule," and "Outdoor, Underground Piping Insulation Schedule" articles.

Condensate drain piping, [indoors] [and] [outdoors].

Chilled-water and brine piping, [indoors] [and] [outdoors].

Condenser-water piping, [indoors when used for water-side economizer or for condensate control] [and] [outdoors].

Heating hot-water piping, [indoors] [and] [outdoors].

Steam and steam condensate piping, [indoors] [and] [outdoors].

Refrigerant suction and hot-gas piping, [indoors] [and] [outdoors].

Dual-service heating and cooling piping, [indoors] [and] [outdoors].

Heat-recovery piping, [indoors] [and] [outdoors].

Heated fuel-oil piping, [indoors] [and] [outdoors].

Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 230713 "Duct Insulation."

Section 230716 "HVAC Equipment Insulation."

Section 232113.13 "Underground Hydronic Piping" for loose-fill pipe insulation in underground piping outside the building.

Section 336313 "Underground Steam and Condensate Distribution Piping" for loose-fill pipe insulation in underground piping outside the building.

ACTION SUBMITTALS

Product Data: For each type of product indicated. Include thermal conductivity, water-vapor permeance thickness, and jackets (both factory and field applied if any).

Sustainable Design Submittals:

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for adhesives.

Product Data: For adhesives, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for adhesives.

Laboratory Test Reports: For adhesives, indicating compliance with requirements for low-emitting materials.

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for paints and coatings.

Product Data: For coatings, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for paints and coatings.

Laboratory Test Reports: For coatings, indicating compliance with requirements for low-emitting materials.

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for sealants.

Product Data: For sealants, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for sealants.

Laboratory Test Reports: For sealants, indicating compliance with requirements for low-emitting materials.

Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

Detail application of protective shields, saddles, and inserts at hangers for each type of insulation and hanger.

Detail attachment and covering of heat tracing inside insulation.

Detail insulation application at pipe expansion joints for each type of insulation.

Detail insulation application at elbows, fittings, flanges, valves, and specialties for each type of insulation.

Detail removable insulation at piping specialties.

Detail application of field-applied jackets.

Detail application at linkages of control devices.

Retain paragraph below to verify products with Samples.

Samples: For each type of insulation and jacket indicated. Identify each Sample, describing product and intended use.

Preformed Pipe Insulation Materials: 12 inches (300 mm) long by NPS 2 (DN 50).

Sheet Form Insulation Materials: 12 inches (300 mm) square.

Jacket Materials for Pipe: 12 inches (300 mm) long by NPS 2 (DN 50).

Sheet Jacket Materials: 12 inches (300 mm) square.

Manufacturer's Color Charts: For products where color is specified, show the full range of colors available for each type of finish material.

INFORMATIONAL SUBMITTALS

Coordinate first paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

Qualification Data: For qualified Installer.

Retain first paragraph below if surface-burning characteristics specified in "Quality Assurance" Article are specified to be verified by an independent testing agency.

Material Test Reports: From a qualified testing agency acceptable to authorities having jurisdiction indicating, interpreting, and certifying test results for compliance of insulation materials, sealers, attachments, cements, and jackets, with requirements indicated. Include dates of tests and test methods employed.

Retain paragraph below if Contractor is responsible for field quality-control testing and inspecting.

Field quality-control reports.

QUALITY ASSURANCE

Retain first paragraph below if available at Project location. Apprenticeship programs are usually associated with union shops. Other craft training programs are available.

Installer Qualifications: Skilled mechanics who have successfully completed an apprenticeship program or another craft training program certified by the Department of Labor, Bureau of Apprenticeship and Training. Preference will be given to those who have successfully completed a manufacturer's installation training program, such as the 'Armacell Qualified Installer Program' (AQIP) or similar.

Inspection: A certified mechanical insulation shall be performed by inspectors who maintain current certification, by the National Insulation Association or other certified mechanical association, throughout the project to inspect and verify the materials and the total insulation system has been installed correctly in accordance with the specifications and material manufacturer’s instructions.

When fire-performance characteristics are important requirements, verify surface-burning characteristics of insulation materials by an independent testing agency and require test report submittals.

Surface-Burning Characteristics: For insulation and related materials, as determined by testing identical products listed and labeled in accordance with UL 723 or in accordance with ASTM E 84, by a testing and inspecting agency acceptable to authorities having jurisdiction. Factory label insulation and jacket materials and adhesive, mastic, tapes, and cement material containers, with appropriate markings of applicable testing agency.

Insulation Installed Indoors: Flame-spread index of 25 or less, and smoke-developed index of 50 or less.

Insulation Installed Outdoors: Flame-spread index of 75 or less, and smoke-developed index of 150 or less.

If retaining "Mockups" Paragraph below, indicate location, size, and other details of mockups on Drawings or by inserts. Revise if only one mockup is required.

Mockups: Before installing insulation, build mockups for each type of insulation and finish listed below to demonstrate quality of insulation application and finishes. Build mockups in the location indicated or, if not indicated, as directed by Architect. Use materials indicated for the completed Work.

Piping Mockups:

One 10-foot (3-m) section of NPS 2 (DN 50) straight pipe.

One each of a 90-degree threaded, welded, and flanged elbow.

One each of a threaded, welded, and flanged tee fitting.

One NPS 2 (DN 50) or smaller valve, and one NPS 2-1/2 (DN 65) or larger valve.

Four support hangers including hanger shield and insert.

One threaded strainer and one flanged strainer with removable portion of insulation.

One threaded reducer and one welded reducer.

One pressure temperature tap.

One mechanical coupling.

For each mockup, fabricate cutaway sections to allow observation of application details for insulation materials, adhesives, mastics, attachments, and jackets.

Notify Architect seven days in advance of dates and times when mockups will be constructed.

Obtain Architect's approval of mockups before starting insulation application.

Retain first subparagraph below if mockups are not only for establishing appearance factors.

Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

Demolish and remove mockups when directed.

DELIVERY, STORAGE, AND HANDLING

Retain this article to require shipping container markings. Container marking is an option in ASTM standards; default condition does not include the marking in this article unless specified in the Contract.

Packaging: Insulation material containers shall be marked by manufacturer with appropriate ASTM standard designation, type and grade, and maximum use temperature.

COORDINATION

Coordinate sizes and locations of supports, hangers, and insulation shields specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

Coordinate clearance requirements with piping Installer for piping insulation application. Before preparing piping Shop Drawings, establish and maintain clearance requirements for installation of insulation and field-applied jackets and finishes and for space required for maintenance.

Coordinate installation and testing of heat tracing.

SCHEDULING

Schedule insulation application after pressure testing systems and, where required, after installing and testing heat tracing. Insulation application may begin on segments that have satisfactory test results.

Complete installation and concealment of plastic materials as rapidly as possible in each area of construction.

PRODUCTS

INSULATION MATERIALS

If retaining more than one type of insulation in this article, indicate where each type applies in insulation system schedules.

Comply with requirements in "Piping Insulation Schedule, General," "Indoor Piping Insulation Schedule," "Outdoor, Aboveground Piping Insulation Schedule," and "Outdoor, Underground Piping Insulation Schedule" articles for where insulating materials shall be applied.

See "Product Characteristics" Article in Evaluations for comparisons and temperature ranges for insulation material properties.

Products shall not contain asbestos, lead, mercury, or mercury compounds.

Products that come in contact with stainless steel shall have a leachable chloride content of less than 50 ppm when tested according to ASTM C 871.

Insulation materials for use on austenitic stainless steel shall be qualified as acceptable according to ASTM C 795.

Foam insulation materials shall not use CFC or HCFC blowing agents in the manufacturing process.

Calcium Silicate:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Industrial Insulation Group, LLC (IIG-LLC).

<Insert manufacturer's name>.

Preformed Pipe Sections: Flat-, curved-, and grooved-block sections of noncombustible, inorganic, hydrous calcium silicate with a non-asbestos fibrous reinforcement. Comply with ASTM C 533, Type I.

Flat-, curved-, and grooved-block sections of noncombustible, inorganic, hydrous calcium silicate with a non-asbestos fibrous reinforcement. Comply with ASTM C 533, Type I.

Prefabricated Fitting Covers: Comply with ASTM C 450 and ASTM C 585 for dimensions used in preforming insulation to cover valves, elbows, tees, and flanges.

Cellular Glass: Inorganic, incombustible, foamed or cellulated glass with annealed, rigid, hermetically sealed cells. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Pittsburgh Corning Corporation.

<Insert manufacturer's name>.

Block Insulation: ASTM C 552, Type I.

Special-Shaped Insulation: ASTM C 552, Type III.

Board Insulation: ASTM C 552, Type IV.

If retaining both types of insulation in first two subparagraphs below, indicate where each type applies in insulation system schedules.

Preformed Pipe Insulation without Jacket: Comply with ASTM C 552, Type II, Class 1.

Preformed Pipe Insulation with Factory-Applied [ASJ] [ASJ-SSL]: Comply with ASTM C 552, Type II, Class 2.

Factory fabricate shapes according to ASTM C 450 and ASTM C 585.

Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C 534, Grade 1, Type I for tubular materials. UL Classified to UL 723 at 25/50.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

AP Armaflex is our standard tube insulation. AP Armaflex Black LapSeal comes with a pre-made longitudinal cut and adhesive, making it easier to install in straight sections.

Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaFlex Ultra] [or] [ArmaFlex Ultra SA] or a comparable product by one of the following:

Aeroflex USA, Inc.

K-Flex USA.

<Insert manufacturer's name>.

Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C 534, Grade 1, Type I for tubular materials.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

AP Armaflex is our standard tube insulation. AP Armaflex Black LapSeal comes with a pre-made longitudinal cut and adhesive, making it easier to install in straight sections.

Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [AP ArmaFlex] [or] [AP ArmaFlex Black LapSeal] or a comparable product by one of the following:

Aeroflex USA, Inc.

K-Flex USA.

<Insert manufacturer's name>.

Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C 534, Grade 1, Type I for tubular materials.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

ArmaFlex UT is a high-temperature FEF with some UV resistance. It was made for variable refrigerant flow (VRF) systems, variable refrigerant volume (VRV) systems, dual temperature systems, hot gas piping, solar applications, low-pressure steam lines, and stainless-steel applications. Maximum temperature of 300 deg F (149 deg C).

Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaFlex UT] [or] [ArmaFlex UT LapSeal] or a comparable product by one of the following:

Aeroflex USA, Inc.

K-Flex USA.

<Insert manufacturer's name>.

Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials with factory-applied polymeric protective covering. Comply with ASTM C 534, Grade 1, Type I for tubular materials.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

ArmaFlex Shield is a pre-jacketed flexible insulation with a tough moisture and UV resistant coating for outdoor applications.

Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaFlex Shield] or a comparable product by one of the following:

Aeroflex USA, Inc.

K-Flex USA.

<Insert manufacturer's name>.

Mineral-Fiber, Preformed Pipe Insulation:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Johns Manville; a Berkshire Hathaway company.

Knauf Insulation.

Manson Insulation Inc.

Owens Corning.

<Insert manufacturer's name>.

For operating temperatures higher than 850 deg F (454 deg C), delete first subparagraph below and retain second subparagraph. ASJ requires field-applied adhesive and staples. ASJ-SSL does not require field-applied adhesive and staples, resulting in reduced installation labor.

Type I, 850 deg F (454 deg C) Materials: Mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C 547, Type I, Grade A, [without factory-applied jacket] [with factory-applied ASJ] [with factory-applied ASJ-SSL]. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

Type II, 1200 deg F (649 deg C) Materials: Mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C 547, Type II, Grade A, [without factory-applied jacket] [with factory-applied ASJ] [with factory-applied ASJ-SSL]. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

Pipe and tank insulation is used for large-diameter piping and vessels. ASJ is commonly used.

Mineral-Fiber, Pipe and Tank Insulation: Mineral or glass fibers bonded with a thermosetting resin. Semirigid board material with factory-applied [ASJ] [FSK jacket] complying with ASTM C 1393, Type II or Type IIIA Category 2, or with properties similar to ASTM C 612, Type IB. Nominal density is 2.5 lb/cu. ft. (40 kg/cu. m) or more. Thermal conductivity (k-value) at 100 deg F (55 deg C) is 0.29 Btu x in./h x sq. ft. x deg F (0.042 W/m x K) or less. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

CertainTeed Corporation.

Johns Manville; a Berkshire Hathaway company.

Knauf Insulation.

Manson Insulation Inc.

Owens Corning.

<Insert manufacturer's name>.

Polyolefin: Unicellular, polyethylene thermal plastic insulation. Comply with ASTM C 1427, Type I, Grade 1 for tubular materials and Type II, Grade 1 for sheet materials.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Tubolit is semi-split, Tubolit SS has a self-sealing system.

Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [Tubolit] [or] [Tubolit SS] [or] [Imcoa] [or] [Tundra] or a comparable product by one of the following:

<Insert manufacturer's name>.

INSULATING CEMENTS

Mineral-fiber insulating cement is suitable for temperatures from 100 to 1600 deg F (38 to 871 deg C). Vermiculite insulating cement is suitable for temperatures from 100 to 1800 deg F (38 to 982 deg C).

Mineral-Fiber Insulating Cement: Comply with ASTM C 195.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Ramco Insulation, Inc.

<Insert manufacturer's name>.

Expanded or Exfoliated Vermiculite Insulating Cement: Comply with ASTM C 196.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Ramco Insulation, Inc.

<Insert manufacturer's name>.

Mineral-fiber, hydraulic-setting cement is suitable for temperatures from 100 to 1200 deg F (38 to 649 deg C) and for a smooth surface.

Mineral-Fiber, Hydraulic-Setting Insulating and Finishing Cement: Comply with ASTM C 449.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Ramco Insulation, Inc.

<Insert manufacturer's name>.

ADHESIVES

Military Specification in this article was the only standard available when this Section was written. MIL-A-3316C was last updated in October 1987.

Materials shall be compatible with insulation materials, jackets, and substrates and for bonding insulation to itself and to surfaces to be insulated unless otherwise indicated.

Product attributes in first paragraph below are based on Foster Brand products; there are variations among manufacturers.

Calcium Silicate Adhesive: Fibrous, sodium-silicate-based adhesive with a service temperature range of 50 to 800 deg F (10 to 427 deg C).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Eagle Bridges - Marathon Industries.

Foster Brand; H. B. Fuller Construction Products.

Mon-Eco Industries, Inc.

Vimasco Corporation.

<Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for adhesives for porous materials other than wood.

Adhesives shall have a VOC content of [50] <Insert value> g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Cellular-Glass Adhesive: Two-component, thermosetting urethane adhesive containing no flammable solvents, with a service temperature range of minus 100 to plus 200 deg F (minus 73 to plus 93 deg C).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Foster Brand; H. B. Fuller Construction Products.

<Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for adhesives for porous materials other than wood.

Adhesives shall have a VOC content of [50] <Insert value> g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Flexible Elastomeric and Polyolefin Adhesive: Comply with MIL-A-24179A, Type II, Class I.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaFlex 520 Adhesive] or a comparable product by one of the following:

Aeroflex USA, Inc.

Foster Brand; H. B. Fuller Construction Products.

K-Flex USA.

<Insert manufacturer's name>.

Flexible Elastomeric and Polyolefin Adhesive: Comply with SCAQMD Rule 1168.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

The following low VOC adhesives are suitable for LEED and other sustainable system requirements.

Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaFlex 520 Black Low VOC Adhesive] or a comparable product by one of the following:

Aeroflex USA, Inc.

Foster Brand; H. B. Fuller Construction Products.

K-Flex USA.

<Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for plastic foam adhesives.

Adhesives shall have a VOC content of [50] <Insert value> g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

Adhesive shall comply with the testing and product requirements of the MAS Certified Green Program.

Flexible Elastomeric and Polyolefin Adhesive: High Temperature.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

The following high temperature adhesive is for Armacell ArmaFlex UT.

Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [HT 625 Insulation Adhesive] or a comparable product by one of the following:

Aeroflex USA, Inc.

Foster Brand; H. B. Fuller Construction Products.

K-Flex USA.

<Insert manufacturer's name>.

Mineral-Fiber Adhesive: Comply with MIL-A-3316C, Class 2, Grade A.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Eagle Bridges - Marathon Industries.

Foster Brand; H. B. Fuller Construction Products.

Mon-Eco Industries, Inc.

<Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for fiberglass.

Fiberglass adhesive shall have a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

ASJ Adhesive, and FSK and PVDC Jacket Adhesive: Comply with MIL-A-3316C, Class 2, Grade A for bonding insulation jacket lap seams and joints.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Eagle Bridges - Marathon Industries.

Foster Brand; H. B. Fuller Construction Products.

Mon-Eco Industries, Inc.

<Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for contact adhesive.

Adhesive shall have a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

PVC Jacket Adhesive: Compatible with PVC jacket.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Dow Corning Corporation.

Johns Manville; a Berkshire Hathaway company.

P.I.C. Plastics, Inc.

Speedline Corporation.

<Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for contact adhesive.

Adhesive shall have a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

MASTICS

The industry does not have a clear definition that categorizes mastics into vapor barriers, vapor retarders, and breather mastics. Specification follows the nomenclature used by Foster. Products with a perm rating of 0.1 and lower are considered vapor barriers. Products with a perm rating greater than 0.1 and less than 1.0 are considered vapor retarders. Products with a perm rating greater than 1.0 are called "breathable." Consider ambient conditions and operating temperatures when selecting a mastic. Consider using water-based mastics for environmental reasons.

Materials shall be compatible with insulation materials, jackets, and substrates; comply with MIL-PRF-19565C, Type II.

"VOC Content" Subparagraph below applies to LEED 2009 NC, CI, and CS Credit IEQ 4.2.

VOC Content: [300] <Insert value> g/L or less.

"Low-Emitting Materials" Subparagraph below applies to LEED 2009 for Schools.

Low-Emitting Materials: Mastic coatings shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Verify that products listed comply with water-vapor permeance. Require proof of performance and certified test reports from vapor-barrier mastic manufacturer, to support product literature claims.

Retain one of four mastic paragraphs below. Product attributes in first paragraph are based on Foster; there are variations among manufacturers.

Vapor-Barrier Mastic: Water based; suitable for indoor use on below-ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Foster Brand; H. B. Fuller Construction Products.

Knauf Insulation.

Vimasco Corporation.

<Insert manufacturer's name>.

Water-Vapor Permeance: ASTM E 96/E 96M, Procedure B, 0.013 perm (0.009 metric perm) at 43-mil (1.09-mm) dry film thickness.

Service Temperature Range: Minus 20 to plus 180 deg F (Minus 29 to plus 82 deg C).

Solids Content: ASTM D 1644, 58 percent by volume and 70 percent by weight.

Color: White.

Vapor-Barrier Mastic: Solvent based; suitable for indoor use on below-ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Eagle Bridges - Marathon Industries.

Foster Brand; H. B. Fuller Construction Products.

Mon-Eco Industries, Inc.

<Insert manufacturer's name>.

Water-Vapor Permeance: ASTM F 1249, 0.05 perm (0.03 metric perm) at 35-mil (0.9-mm) dry film thickness.

Service Temperature Range: 0 to 180 deg F (Minus 18 to plus 82 deg C).

Solids Content: ASTM D 1644, 44 percent by volume and 62 percent by weight.

Color: White.

Vapor-Barrier Mastic: Solvent based; suitable for outdoor use on below-ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Eagle Bridges - Marathon Industries.

Foster Brand; H. B. Fuller Construction Products.

<Insert manufacturer's name>.

Water-Vapor Permeance: ASTM F 1249, 0.05 perm (0.033 metric perm) at 30-mil (0.8-mm) dry film thickness.

Service Temperature Range: Minus 50 to plus 220 deg F (Minus 46 to plus 104 deg C).

Solids Content: ASTM D 1644, 33 percent by volume and 46 percent by weight.

Color: White.

Breather Mastic: Water based; suitable for indoor and outdoor use on above-ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Eagle Bridges - Marathon Industries.

Foster Brand; H. B. Fuller Construction Products.

Knauf Insulation.

Mon-Eco Industries, Inc.

Vimasco Corporation.

<Insert manufacturer's name>.

Water-Vapor Permeance: ASTM F 1249, 1.8 perms (1.2 metric perms) at 0.0625-inch (1.6-mm) dry film thickness.

Service Temperature Range: Minus 20 to plus 180 deg F (Minus 29 to plus 82 deg C).

Solids Content: 60 percent by volume and 66 percent by weight.

Color: White.

LAGGING ADHESIVES

Description: Comply with MIL-A-3316C, Class I, Grade A and shall be compatible with insulation materials, jackets, and substrates.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Foster Brand; H. B. Fuller Construction Products.

Vimasco Corporation.

<Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for adhesives for porous materials other than wood.

Adhesives shall have a VOC content of [50] <Insert value> g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Fire-resistant, water-based lagging adhesive and coating for use indoors to adhere fire-resistant lagging cloths over pipe insulation.

Service Temperature Range: 0 to plus 180 deg F (Minus 18 to plus 82 deg C).

Color: White.

SEALANTS

Sealants are categorized into "joint sealants" and "flashing sealants." Joint sealants are primarily used for vapor sealing longitudinal seams and butt joints of insulation materials. Flashing sealants are primarily used for sealing jacket and mastic materials.

Cellular-Glass Joint Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Eagle Bridges - Marathon Industries.

Foster Brand; H. B. Fuller Construction Products.

Mon-Eco Industries, Inc.

Pittsburgh Corning Corporation.

<Insert manufacturer's name>.

FSK and Metal Jacket Flashing Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Childers Brand; H. B. Fuller Construction Products.

Eagle Bridges - Marathon Industries.

Foster Brand; H. B. Fuller Construction Products.

Mon-Eco Industries, Inc.

<Insert manufacturer's name>.

Materials shall be compatible with insulation materials, jackets, and substrates.

Fire- and water-resistant, flexible, elastomeric sealant.

Service Temperature Range: Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

Color: Aluminum.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes.

Sealant shall have a VOC content of 420 g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

ASJ Flashing Sealants, and Vinyl, PVDC, and PVC Jacket Flashing Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Childers Brand; H. B. Fuller Construction Products.

<Insert manufacturer's name>.

Materials shall be compatible with insulation materials, jackets, and substrates.

Fire- and water-resistant, flexible, elastomeric sealant.

Service Temperature Range: Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

Color: White.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes.

Sealant shall have a VOC content of 420 g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

FACTORY-APPLIED JACKETS

Coordinate types of factory-applied jacket insulation materials selected and types of factory-applied jackets indicated in insulation system schedules.

For insulation materials with factory-applied jackets for use on applications above 140 deg F (60 deg C), specify sufficient insulation thickness to maintain outer surface temperature of insulation below 140 deg F (60 deg C). 140 deg F (60 deg C) surface temperature is set by OSHA for personnel protection.

CertainTeed and Johns Manville offer a vinyl jacket, but it does not comply with ASTM C 1136. Knauf and Owens Corning do not offer a vinyl product.

Insulation system schedules indicate factory-applied jackets on various applications. When factory-applied jackets are indicated, comply with the following:

ASJ: White, kraft-paper, fiberglass-reinforced scrim with aluminum-foil backing; complying with ASTM C 1136, Type I.

ASJ-SSL: ASJ with self-sealing, pressure-sensitive, acrylic-based adhesive covered by a removable protective strip; complying with ASTM C 1136, Type I.

PVDC and PVDC-SSL jackets in subparagraphs below are proprietary products offered by Dow Chemical under the product names "Saran 540 Vapor Retarder Film" and "Saran 560 Vapor Retarder Film."

PVDC Jacket for Indoor Applications: 4-mil- (0.10-mm-) thick, white PVDC biaxially oriented barrier film with a permeance at 0.02 perm (0.013 metric perm) when tested according to ASTM E 96/E 96M and with a flame-spread index of 5 and a smoke-developed index of 20 when tested according to ASTM E 84.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

<Insert manufacturer's name>.

PVDC Jacket for Outdoor Applications: 6-mil- (0.15-mm-) thick, white PVDC biaxially oriented barrier film with a permeance at 0.01 perm (0.007 metric perm) when tested according to ASTM E 96/E 96M and with a flame-spread index of 5 and a smoke-developed index of 25 when tested according to ASTM E 84.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

<Insert manufacturer's name>.

PVDC-SSL Jacket: PVDC jacket with a self-sealing, pressure-sensitive, acrylic-based adhesive covered by a removable protective strip.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

<Insert manufacturer's name>.

Vinyl Jacket: White vinyl with a permeance of 1.3 perms (0.86 metric perms) when tested according to ASTM E 96/E 96M, Procedure A, and complying with NFPA 90A and NFPA 90B.

FIELD-APPLIED FABRIC-REINFORCING MESH

Both glass-fiber- and polyester-fabric-reinforcing meshes are acceptable.

Retain both paragraphs below to give Contractor option to use either glass-fiber or polyester fabric.

Woven Glass-Fiber Fabric: Approximately 2 oz./sq. yd. (68 g/sq. m) with a thread count of 10 strands by 10 strands/sq. in. (4 strands by 4 strands/sq. mm) for covering pipe and pipe fittings.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Childers Brand; H. B. Fuller Construction Products.

<Insert manufacturer's name>.

Woven Polyester Fabric: Approximately 1 oz./sq. yd. (34 g/sq. m) with a thread count of 10 strands by 10 strands/sq. in. (4 strands by 4 strands/sq. mm), in a Leno weave, for pipe.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Foster Brand; H. B. Fuller Construction Products.

Vimasco Corporation.

<Insert manufacturer's name>.

FIELD-APPLIED CLOTHS

Woven Glass-Fiber Fabric: Comply with MIL-C-20079H, Type I, plain weave, and presized a minimum of 8 oz./sq. yd. (271 g/sq. m).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Alpha Associates, Inc.

<Insert manufacturer's name>.

FIELD-APPLIED JACKETS

Insulation jackets in this article are for field application. ASTM C 921, Type I, is for use over insulation on pipes operating at below-ambient temperatures at least part of the time or where a vapor barrier is required. ASTM C 921, Type II, is for use over insulation on pipes operating above-ambient temperatures or where a vapor retarder is not required.

Field-applied jackets shall comply with ASTM C 921, Type I, unless otherwise indicated.

Although other thicknesses for PVC jackets are available, a flame-spread index of 25 and a smoke-developed index of 50 apply only to thicknesses of 30 mils (0.8 mm) and less.

PVC Jacket: High-impact-resistant, UV-resistant PVC complying with ASTM D 1784, Class 16354-C; thickness as scheduled; roll stock ready for shop or field cutting and forming. Thickness is indicated in field-applied jacket schedules.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Airex Manufacturing.

Johns Manville; a Berkshire Hathaway company.

P.I.C. Plastics, Inc.

Proto Corporation.

Speedline Corporation.

<Insert manufacturer's name>.

Adhesive: As recommended by jacket material manufacturer.

PVC jackets are available in several colors. Colored jackets may be used to replace field painting. UV rays fade colors in exterior applications. Some colors (black, gray, and white) do not fade as quickly as other colors (red, orange, and green). Colored jackets have different emissivity and are not recommended for outdoor use.

Color: [White] [Color-code jackets based on system. Color as selected by Architect].

Factory-fabricated fitting covers to match jacket if available; otherwise, field fabricate.

Shapes: 45- and 90-degree, short- and long-radius elbows, tees, valves, flanges, unions, reducers, end caps, soil-pipe hubs, traps, mechanical joints, and P-trap and supply covers for lavatories.

Metal Jacket:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

RPR Products, Inc.

<Insert manufacturer's name>.

Aluminum Jacket: Comply with ASTM B 209 (ASTM B 209M), Alloy 3003, 3005, 3105, or 5005, Temper H-14.

[Sheet and roll stock ready for shop or field sizing] [Factory cut and rolled to size].

Finish and thickness are indicated in field-applied jacket schedules.

Among the three moisture barriers in first subparagraph below, 1-mil (0.025-mm) barrier provides the least protection against galvanic corrosion, 3-mil (0.075-mm) barrier offers better protection, and polysurlyn barrier offers the best protection. For most indoor applications, 1-mil (0.025-mm) barrier is adequate. For outdoor applications, select either 3-mil (0.075-mm) or polysurlyn barrier.

Moisture Barrier for Indoor Applications: [1-mil- (0.025-mm-) thick, heat-bonded polyethylene and kraft paper] [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

Moisture Barrier for Outdoor Applications: [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

Factory-Fabricated Fitting Covers:

Same material, finish, and thickness as jacket.

Preformed 2-piece or gore, 45- and 90-degree, short- and long-radius elbows.

Tee covers.

Flange and union covers.

End caps.

Beveled collars.

Valve covers.

Field fabricate fitting covers only if factory-fabricated fitting covers are not available.

Stainless-Steel Jacket: ASTM A 167 or ASTM A 240/A 240M.

[Sheet and roll stock ready for shop or field sizing] [Factory cut and rolled to size].

Material, finish, and thickness are indicated in field-applied jacket schedules.

Among the three moisture barriers in first subparagraph below, 1-mil (0.025-mm) barrier provides the least protection against galvanic corrosion, 3-mil (0.075-mm) barrier offers better protection, and polysurlyn barrier offers the best protection. For most indoor applications, 1-mil (0.025-mm) barrier is adequate.

Moisture Barrier for Indoor Applications: [1-mil- (0.025-mm-) thick, heat-bonded polyethylene and kraft paper] [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

Moisture Barrier for Outdoor Applications: [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

Factory-Fabricated Fitting Covers:

Same material, finish, and thickness as jacket.

Preformed 2-piece or gore, 45- and 90-degree, short- and long-radius elbows.

Tee covers.

Flange and union covers.

End caps.

Beveled collars.

Valve covers.

Field fabricate fitting covers only if factory-fabricated fitting covers are not available.

Underground Direct-Buried Jacket: 125-mil- (3.2-mm-) thick vapor barrier and waterproofing membrane consisting of a rubberized bituminous resin reinforced with a woven-glass fiber or polyester scrim and laminated aluminum foil.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Pittsburgh Corning Corporation.

Polyguard Products, Inc.

<Insert manufacturer's name>.

Self-Adhesive Outdoor Jacket: 60-mil- (1.5-mm-) thick, laminated vapor barrier and waterproofing membrane for installation over insulation located aboveground outdoors; consisting of a rubberized bituminous resin on a cross-laminated polyethylene film covered with [white] [stucco-embossed] aluminum-foil facing.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

Polyguard Products, Inc.

<Insert manufacturer's name>.

PVDC and PVDC-SSL jackets in three paragraphs below are proprietary products offered by Dow Chemical under the product names "Saran 540 Vapor Retarder Film" and "Saran 560 Vapor Retarder Film."

PVDC Jacket for Indoor Applications: 4-mil- (0.10-mm-) thick, white PVDC biaxially oriented barrier film with a permeance at 0.02 perms (0.013 metric perms) when tested according to ASTM E 96/E 96M and with a flame-spread index of 5 and a smoke-developed index of 20 when tested according to ASTM E 84.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

<Insert manufacturer's name>.

PVDC Jacket for Outdoor Applications: 6-mil- (0.15-mm-) thick, white PVDC biaxially oriented barrier film with a permeance at 0.01 perms (0.007 metric perms) when tested according to ASTM E 96/E 96M and with a flame-spread index of 5 and a smoke-developed index of 25 when tested according to ASTM E 84.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

<Insert manufacturer's name>.

PVDC-SSL Jacket: PVDC jacket with a self-sealing, pressure-sensitive, acrylic-based adhesive covered by a removable protective strip.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

<Insert manufacturer's name>.

TAPES

Seal Tape: Self-adhering tape specifically engineered to cover butt joints of self-adhering elastomeric tube material.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaFlex Black LapSeal Tape] or a comparable product by one of the following:

Aeroflex USA, Inc.

K-Flex USA.

<Insert manufacturer's name>.

Product performance for ASJ Tape below is based on products manufactured by Venture Tape; there are slight variations among manufacturers.

ASJ Tape: White vapor-retarder tape matching factory-applied jacket with acrylic adhesive, complying with ASTM C 1136.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Avery Dennison Corporation, Specialty Tapes Division.

Compac Corporation.

Ideal Tape Co., Inc., an American Biltrite Company.

Knauf Insulation.

Venture Tape.

<Insert manufacturer's name>.

Width: 3 inches (75 mm).

Thickness: 11.5 mils (0.29 mm).

Adhesion: 90 ounces force/inch (1.0 N/mm) in width.

Elongation: 2 percent.

Tensile Strength: 40 lbf/inch (7.2 N/mm) in width.

ASJ Tape Disks and Squares: Precut disks or squares of ASJ tape.

PVC Tape: White vapor-retarder tape matching field-applied PVC jacket with acrylic adhesive; suitable for indoor and outdoor applications.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Compac Corporation.

Ideal Tape Co., Inc., an American Biltrite Company.

Venture Tape.

<Insert manufacturer's name>.

Width: 2 inches (50 mm).

Thickness: 6 mils (0.15 mm).

Adhesion: 64 ounces force/inch (0.7 N/mm) in width.

Elongation: 500 percent.

Tensile Strength: 18 lbf/inch (3.3 N/mm) in width.

Aluminum-Foil Tape: Vapor-retarder tape with acrylic adhesive.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Avery Dennison Corporation, Specialty Tapes Division.

Compac Corporation.

Ideal Tape Co., Inc., an American Biltrite Company.

Knauf Insulation.

Venture Tape.

<Insert manufacturer's name>.

Width: 2 inches (50 mm).

Thickness: 3.7 mils (0.093 mm).

Adhesion: 100 ounces force/inch (1.1 N/mm) in width.

Elongation: 5 percent.

Tensile Strength: 34 lbf/inch (6.2 N/mm) in width.

PVDC tape is a proprietary product offered by Dow Chemical under the product names "Saran 540 Vapor Retarder Tape" and "Saran 560 Vapor Retarder Tape."

PVDC Tape for Indoor Applications: White vapor-retarder PVDC tape with acrylic adhesive.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

<Insert manufacturer's name>.

Width: 3 inches (75 mm).

Film Thickness: 4 mils (0.10 mm).

Adhesive Thickness: 1.5 mils (0.04 mm).

Elongation at Break: 145 percent.

Tensile Strength: 55 lbf/inch (10.1 N/mm) in width.

PVDC Tape for Outdoor Applications: White vapor-retarder PVDC tape with acrylic adhesive.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

<Insert manufacturer's name>.

Width: 3 inches (75 mm).

Film Thickness: 6 mils (0.15 mm).

Adhesive Thickness: 1.5 mils (0.04 mm).

Elongation at Break: 145 percent.

Tensile Strength: 55 lbf/inch (10.1 N/mm) in width.

SECUREMENTS

Bands:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ITW Insulation Systems; Illinois Tool Works, Inc.

RPR Products, Inc.

<Insert manufacturer's name>.

Wing seals are primarily used for fastening bands together. Closed seals are occasionally used for large, 84-inch- (2130-mm-) diameter applications and where fastening bands are used with springs. Wing seals are reusable; closed seals are not.

Stainless Steel: ASTM A 167 or ASTM A 240/A 240M, [Type 304] [or] [Type 316]; 0.015 inch (0.38 mm) thick, [1/2 inch (13 mm)] [3/4 inch (19 mm)] wide with [wing seal] [or] [closed seal].

Aluminum: ASTM B 209 (ASTM B 209M), Alloy 3003, 3005, 3105, or 5005; Temper H-14, 0.020 inch (0.51 mm) thick, [1/2 inch (13 mm)] [3/4 inch (19 mm)] wide with [wing seal] [or] [closed seal].

Springs are used for large, 84-inch- (2130-mm-) diameter applications and on applications with rapid changes in expansion and contraction.

Springs: Twin spring set constructed of stainless steel with ends flat and slotted to accept metal bands. Spring size determined by manufacturer for application.

Staples: Outward-clinching insulation staples, nominal 3/4-inch- (19-mm-) wide, stainless steel or Monel.

In paragraph below, stainless steel is the most common wire used and is best suited for all applications.

Wire: [0.080-inch (2.0-mm) nickel-copper alloy] [0.062-inch (1.6-mm) soft-annealed, stainless steel] [0.062-inch (1.6-mm) soft-annealed, galvanized steel].

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, provide products by the following:

C & F Wire.

<Insert manufacturer's name>.

EXECUTION

EXAMINATION

Examine substrates and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of insulation application.

Verify that systems to be insulated have been tested and are free of defects.

Verify that surfaces to be insulated are clean and dry.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Retain one of first two paragraphs below. Corrosion of metal pipe under insulation, while not typically caused by insulation, is an issue that must be considered during design of any HVAC insulation system. The potential for corrosion depends on many factors. Requirements cited in second paragraph represent added measures of protection but are not meant to take the place of proper system design and specification.

Surface Preparation: Clean and dry surfaces to receive insulation. Remove materials that will adversely affect insulation application.

Surface Preparation: Clean and prepare surfaces to be insulated. Before insulating, apply a corrosion coating to insulated surfaces as follows:

Stainless Steel: Coat 300 series stainless steel with an epoxy primer 5 mils (0.127 mm) thick and an epoxy finish 5 mils (0.127 mm) thick if operating in a temperature range between 140 and 300 deg F (60 and 149 deg C). Consult coating manufacturer for appropriate coating materials and application methods for operating temperature range.

Carbon Steel: Coat carbon steel operating at a service temperature between 32 and 300 deg F (0 and 149 deg C) with an epoxy coating. Consult coating manufacturer for appropriate coating materials and application methods for operating temperature range.

Coordinate insulation installation with the trade installing heat tracing. Comply with requirements for heat tracing that applies to insulation.

Mix insulating cements with clean potable water; if insulating cements are to be in contact with stainless-steel surfaces, use demineralized water.

GENERAL INSTALLATION REQUIREMENTS

Install insulation materials, accessories, and finishes with smooth, straight, and even surfaces; free of voids throughout the length of piping including fittings, valves, and specialties.

Install insulation materials, forms, vapor barriers or retarders, jackets, and thicknesses required for each item of pipe system as specified in insulation system schedules.

Install accessories compatible with insulation materials and suitable for the service. Install accessories that do not corrode, soften, or otherwise attack insulation or jacket in either wet or dry state.

Install insulation with longitudinal seams at top and bottom of horizontal runs.

Install multiple layers of insulation with longitudinal and end seams staggered.

Do not weld brackets, clips, or other attachment devices to piping, fittings, and specialties.

Keep insulation materials dry during application and finishing.

Install insulation with tight longitudinal seams and end joints. Bond seams and joints with adhesive recommended by insulation material manufacturer.

Install insulation with least number of joints practical.

Where vapor barrier is indicated, seal joints, seams, and penetrations in insulation at hangers, supports, anchors, and other projections with vapor-barrier mastic.

Install insulation continuously through hangers and around anchor attachments.

For insulation application where vapor barriers are indicated, extend insulation on anchor legs from point of attachment to supported item to point of attachment to structure. Taper and seal ends at attachment to structure with vapor-barrier mastic.

Install insert materials and install insulation to tightly join the insert. Seal insulation to insulation inserts with adhesive or sealing compound recommended by insulation material manufacturer.

Cover inserts with jacket material matching adjacent pipe insulation. Install shields over jacket, arranged to protect jacket from tear or puncture by hanger, support, and shield.

Apply adhesives, mastics, and sealants at manufacturer's recommended coverage rate and wet and dry film thicknesses.

Install insulation with factory-applied jackets as follows:

Draw jacket tight and smooth.

Cover circumferential joints with 3-inch- (75-mm-) wide strips, of same material as insulation jacket. Secure strips with adhesive and outward clinching staples along both edges of strip, spaced 4 inches (100 mm) o.c.

Overlap jacket longitudinal seams at least 1-1/2 inches (38 mm). Install insulation with longitudinal seams at bottom of pipe.

Cover joints and seams with tape, according to insulation material manufacturer's written instructions, to maintain vapor seal.

Where vapor barriers are indicated, apply vapor-barrier mastic on seams and joints and at ends adjacent to pipe flanges and fittings.

Cut insulation in a manner to avoid compressing insulation more than 75 percent of its nominal thickness.

Finish installation with systems at operating conditions. Repair joint separations and cracking due to thermal movement.

Repair damaged insulation facings by applying same facing material over damaged areas. Extend patches at least 4 inches (100 mm) beyond damaged areas. Adhere, staple, and seal patches similar to butt joints.

For above-ambient services, do not install insulation to the following:

Vibration-control devices.

Testing agency labels and stamps.

Nameplates and data plates.

Manholes.

Handholes.

Cleanouts.

PENETRATIONS

Insulation Installation at Roof Penetrations: Install insulation continuously through roof penetrations.

Seal penetrations with flashing sealant.

For applications requiring only indoor insulation, terminate insulation above roof surface and seal with joint sealant. For applications requiring indoor and outdoor insulation, install insulation for outdoor applications tightly joined to indoor insulation ends. Seal joint with joint sealant.

Extend jacket of outdoor insulation outside roof flashing at least 2 inches (50 mm) below top of roof flashing.

Seal jacket to roof flashing with flashing sealant.

Insulation Installation at Underground Exterior Wall Penetrations: Terminate insulation flush with sleeve seal. Seal terminations with flashing sealant.

Insulation Installation at Aboveground Exterior Wall Penetrations: Install insulation continuously through wall penetrations.

Seal penetrations with flashing sealant.

For applications requiring only indoor insulation, terminate insulation inside wall surface and seal with joint sealant. For applications requiring indoor and outdoor insulation, install insulation for outdoor applications tightly joined to indoor insulation ends. Seal joint with joint sealant.

Extend jacket of outdoor insulation outside wall flashing and overlap wall flashing at least 2 inches (50 mm).

Seal jacket to wall flashing with flashing sealant.

Insulation Installation at Interior Wall and Partition Penetrations (That Are Not Fire Rated): Install insulation continuously through walls and partitions.

Insulation Installation at Fire-Rated Wall and Partition Penetrations: Install insulation continuously through penetrations of fire-rated walls and partitions.

Comply with requirements in Section 078413 "Penetration Firestopping" for firestopping and fire-resistive joint sealers.

Insulation Installation at Floor Penetrations:

Pipe: Install insulation continuously through floor penetrations.

Seal penetrations through fire-rated assemblies. Comply with requirements in Section 078413 "Penetration Firestopping."

GENERAL PIPE INSULATION INSTALLATION

Requirements in this article generally apply to all insulation materials except where more specific requirements are specified in various pipe insulation material installation articles.

Where pipe expansion is anticipated, detail expansion compensation for insulation on Drawings and indicate intervals for its occurrence. See the Midwest Insulation Contractors Association's "National Commercial & Industrial Insulation Standards," Plate No. 41A.

Insulation Installation on Fittings, Valves, Strainers, Flanges, and Unions:

Install insulation over fittings, valves, strainers, flanges, unions, and other specialties with continuous thermal and vapor-retarder integrity unless otherwise indicated.

Insulate pipe elbows using preformed fitting insulation or mitered fittings made from same material and density as adjacent pipe insulation. Each piece shall be butted tightly against adjoining piece and bonded with adhesive. Fill joints, seams, voids, and irregular surfaces with insulating cement finished to a smooth, hard, and uniform contour that is uniform with adjoining pipe insulation.

Insulate tee fittings with preformed fitting insulation or sectional pipe insulation of same material and thickness as used for adjacent pipe. Cut sectional pipe insulation to fit. Butt each section closely to the next and hold in place with tie wire. Bond pieces with adhesive.

Insulate valves using preformed fitting insulation or sectional pipe insulation of same material, density, and thickness as used for adjacent pipe. Overlap adjoining pipe insulation by not less than two times the thickness of pipe insulation, or one pipe diameter, whichever is thicker. For valves, insulate up to and including the bonnets, valve stuffing-box studs, bolts, and nuts. Fill joints, seams, and irregular surfaces with insulating cement.

Insulate strainers using preformed fitting insulation or sectional pipe insulation of same material, density, and thickness as used for adjacent pipe. Overlap adjoining pipe insulation by not less than two times the thickness of pipe insulation, or one pipe diameter, whichever is thicker. Fill joints, seams, and irregular surfaces with insulating cement. Insulate strainers so strainer basket flange or plug can be easily removed and replaced without damaging the insulation and jacket. Provide a removable reusable insulation cover. For below-ambient services, provide a design that maintains vapor barrier.

Insulate flanges and unions using a section of oversized preformed pipe insulation. Overlap adjoining pipe insulation by not less than two times the thickness of pipe insulation, or one pipe diameter, whichever is thicker.

Cover segmented insulated surfaces with a layer of finishing cement and coat with a mastic. Install vapor-barrier mastic for below-ambient services and a breather mastic for above-ambient services. Reinforce the mastic with fabric-reinforcing mesh. Trowel the mastic to a smooth and well-shaped contour.

For services not specified to receive a field-applied jacket except for flexible elastomeric and polyolefin, install fitted PVC cover over elbows, tees, strainers, valves, flanges, and unions. Terminate ends with PVC end caps. Tape PVC covers to adjoining insulation facing using PVC tape.

Stencil or label the outside insulation jacket of each union with the word "union." Match size and color of pipe labels.

Insulate instrument connections for thermometers, pressure gages, pressure temperature taps, test connections, flow meters, sensors, switches, and transmitters on insulated pipes. Shape insulation at these connections by tapering it to and around the connection with insulating cement and finish with finishing cement, mastic, and flashing sealant.

Coordinate paragraph below with Drawings.

Install removable insulation covers at locations indicated. Installation shall conform to the following:

Make removable flange and union insulation from sectional pipe insulation of same thickness as that on adjoining pipe. Install same insulation jacket as adjoining pipe insulation.

When flange and union covers are made from sectional pipe insulation, extend insulation from flanges or union long at least two times the insulation thickness over adjacent pipe insulation on each side of flange or union. Secure flange cover in place with stainless-steel or aluminum bands. Select band material compatible with insulation and jacket.

Construct removable valve insulation covers in same manner as for flanges, except divide the two-part section on the vertical center line of valve body.

When covers are made from block insulation, make two halves, each consisting of mitered blocks wired to stainless-steel fabric. Secure this wire frame, with its attached insulation, to flanges with tie wire. Extend insulation at least 2 inches (50 mm) over adjacent pipe insulation on each side of valve. Fill space between flange or union cover and pipe insulation with insulating cement. Finish cover assembly with insulating cement applied in two coats. After first coat is dry, apply and trowel second coat to a smooth finish.

Unless a PVC jacket is indicated in field-applied jacket schedules, finish exposed surfaces with a metal jacket.

INSTALLATION OF CALCIUM SILICATE INSULATION

Insulation Installation on Straight Pipes and Tubes:

Secure single-layer insulation with stainless-steel bands at 12-inch (300-mm) intervals and tighten bands without deforming insulation materials.

Install two-layer insulation with joints tightly butted and staggered at least 3 inches (75 mm). Secure inner layer with wire spaced at 12-inch (300-mm) intervals. Secure outer layer with stainless-steel bands at 12-inch (300-mm) intervals.

Apply a skim coat of mineral-fiber, hydraulic-setting cement to insulation surface. When cement is dry, apply flood coat of lagging adhesive and press on one layer of glass cloth or tape. Overlap edges at least 1 inch (25 mm). Apply finish coat of lagging adhesive over glass cloth or tape. Thin finish coat to achieve smooth, uniform finish.

Insulation Installation on Pipe Flanges:

Install preformed pipe insulation to outer diameter of pipe flange.

Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of block insulation of same material and thickness as pipe insulation.

Finish flange insulation same as pipe insulation.

Insulation Installation on Pipe Fittings and Elbows:

Install preformed sections of same material as straight segments of pipe insulation when available. Secure according to manufacturer's written instructions.

When preformed insulation sections of insulation are not available, install mitered sections of calcium silicate insulation. Secure insulation materials with wire or bands.

Finish fittings insulation same as pipe insulation.

Insulation Installation on Valves and Pipe Specialties:

Install mitered segments of calcium silicate insulation to valve body. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

Install insulation to flanges as specified for flange insulation application.

Finish valve and specialty insulation same as pipe insulation.

INSTALLATION OF CELLULAR-GLASS INSULATION

Insulation Installation on Straight Pipes and Tubes:

Secure each layer of insulation to pipe with wire or bands and tighten bands without deforming insulation materials.

Where vapor barriers are indicated, seal longitudinal seams, end joints, and protrusions with vapor-barrier mastic and joint sealant.

For insulation with factory-applied jackets on above-ambient services, secure laps with outward-clinched staples at 6 inches (150 mm) o.c.

For insulation with factory-applied jackets on below-ambient services, do not staple longitudinal tabs. Instead, secure tabs with additional adhesive as recommended by insulation material manufacturer and seal with vapor-barrier mastic and flashing sealant.

Insulation Installation on Pipe Flanges:

Install preformed pipe insulation to outer diameter of pipe flange.

Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of cellular-glass block insulation of same thickness as pipe insulation.

Install jacket material with manufacturer's recommended adhesive, overlap seams at least 1 inch (25 mm), and seal joints with flashing sealant.

Insulation Installation on Pipe Fittings and Elbows:

Install preformed sections of same material as straight segments of pipe insulation when available. Secure according to manufacturer's written instructions.

When preformed sections of insulation are not available, install mitered sections of cellular-glass insulation. Secure insulation materials with wire or bands.

Insulation Installation on Valves and Pipe Specialties:

Install preformed sections of cellular-glass insulation to valve body.

Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

Install insulation to flanges as specified for flange insulation application.

INSTALLATION OF FLEXIBLE ELASTOMERIC INSULATION

Installation shall follow the manufacturer's installation instructions or ASTM C 1710.

Insulation Installation on Straight Pipes and Tubes:

Slit tubular sections and apply onto piping or tubing. Alternatively, slide un-slit sections over the open ends of piping or tubing.

Seal longitudinal seams and end joints with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

Insulation must be installed in compression to allow for expansion and contraction.

Insulation shall be pushed onto the pipe, never pulled. Stretching of insulation may result in open seams and joints.

For below-ambient systems, adhere the insulation to the pipe at least every 18 feet (5.5-m) using manufacturer's adhesive. Completely terminate joints at critical points such as flanges, T-sections, elbows, supports, and similar fittings.

Insulation Installation on Pipe Flanges:

Install preformed valve covers manufactured of same material as pipe insulation when available.

Install pipe insulation to outer diameter of pipe flange.

Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of sheet insulation of same thickness as pipe insulation.

Secure insulation to flanges and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

Insulation Installation on Pipe Fittings and Elbows:

Install preformed valve covers manufactured of same material as pipe insulation when available.

Install mitered sections of pipe insulation.

Secure insulation materials and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

Insulation Installation on Valves and Pipe Specialties:

Install preformed valve covers manufactured of same material as pipe insulation when available.

When preformed valve covers are not available, install cut sections of pipe and sheet insulation to valve body. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

Install insulation to flanges as specified for flange insulation application.

Secure insulation to valves and specialties and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

INSTALLATION OF MINERAL-FIBER INSULATION

Insulation Installation on Straight Pipes and Tubes:

Secure each layer of preformed pipe insulation to pipe with wire or bands and tighten bands without deforming insulation materials.

Where vapor barriers are indicated, seal longitudinal seams, end joints, and protrusions with vapor-barrier mastic and joint sealant.

For insulation with factory-applied jackets on above-ambient surfaces, secure laps with outward-clinched staples at 6 inches (150 mm) o.c.

For insulation with factory-applied jackets on below-ambient surfaces, do not staple longitudinal tabs. Instead, secure tabs with additional adhesive as recommended by insulation material manufacturer and seal with vapor-barrier mastic and flashing sealant.

Insulation Installation on Pipe Flanges:

Install preformed pipe insulation to outer diameter of pipe flange.

Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with mineral-fiber blanket insulation.

Install jacket material with manufacturer's recommended adhesive, overlap seams at least 1 inch (25 mm), and seal joints with flashing sealant.

Insulation Installation on Pipe Fittings and Elbows:

Install preformed sections of same material as straight segments of pipe insulation when available.

When preformed insulation elbows and fittings are not available, install mitered sections of pipe insulation, to a thickness equal to adjoining pipe insulation. Secure insulation materials with wire or bands.

Insulation Installation on Valves and Pipe Specialties:

Install preformed sections of same material as straight segments of pipe insulation when available.

When preformed sections are not available, install mitered sections of pipe insulation to valve body.

Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

Install insulation to flanges as specified for flange insulation application.

INSTALLATION OF POLYOLEFIN INSULATION

Installation shall follow the manufacturer's installation instructions or ASTM C 1710.

Insulation Installation on Straight Pipes and Tubes:

Slit tubular sections and apply onto piping or tubing. Alternatively, slide un-slit sections over the open ends of piping or tubing.

Seal split-tube longitudinal seams and end joints with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

Insulation must be installed in compression to allow for expansion and contraction.

Insulation shall be pushed onto the pipe, never pulled. Stretching of insulation may result in open seams and joints.

For below-ambient systems, adhere the insulation to the pipe at least every 18 feet (5.5-m) using manufacturer's adhesive. Completely terminate joints at critical points such as flanges, T-sections, elbows, supports, and similar fittings.

Insulation Installation on Pipe Flanges:

Install pipe insulation to outer diameter of pipe flange.

Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of polyolefin sheet insulation of same thickness as pipe insulation.

Secure insulation to flanges and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

Insulation Installation on Pipe Fittings and Elbows:

Install mitered sections of polyolefin pipe insulation.

Secure insulation materials and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

Insulation Installation on Valves and Pipe Specialties:

Install cut sections of polyolefin pipe and sheet insulation to valve body.

Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

Install insulation to flanges as specified for flange insulation application.

Secure insulation to valves and specialties, and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

FIELD-APPLIED JACKET INSTALLATION

Where glass-cloth jackets are indicated, install directly over bare insulation or insulation with factory-applied jackets.

Draw jacket smooth and tight to surface with 2-inch (50-mm) overlap at seams and joints.

Embed glass cloth between two 0.062-inch- (1.6-mm-) thick coats of lagging adhesive.

Completely encapsulate insulation with coating, leaving no exposed insulation.

Where FSK jackets are indicated, install as follows:

Draw jacket material smooth and tight.

Install lap or joint strips with same material as jacket.

Secure jacket to insulation with manufacturer's recommended adhesive.

Install jacket with 1-1/2-inch (38-mm) laps at longitudinal seams and 3-inch- (75-mm-) wide joint strips at end joints.

Seal openings, punctures, and breaks in vapor-retarder jackets and exposed insulation with vapor-barrier mastic.

Where PVC jackets are indicated, install with 1-inch (25-mm) overlap at longitudinal seams and end joints; for horizontal applications. Seal with manufacturer's recommended adhesive.

Apply two continuous beads of adhesive to seams and joints, one bead under lap and the finish bead along seam and joint edge.

Where metal jackets are indicated, install with 2-inch (50-mm) overlap at longitudinal seams and end joints. Overlap longitudinal seams arranged to shed water. Seal end joints with weatherproof sealant recommended by insulation manufacturer. Secure jacket with stainless-steel bands 12 inches (300 mm) o.c. and at end joints.

Where PVDC jackets are indicated, install as follows:

Apply three separate wraps of filament tape per insulation section to secure pipe insulation to pipe prior to installation of PVDC jacket.

Wrap factory-presized jackets around individual pipe insulation sections with one end overlapping the previously installed sheet. Install presized jacket with an approximate overlap at butt joint of 2 inches (50 mm) over the previous section. Adhere lap seal using adhesive or SSL, and then apply 1-1/4 circumferences of appropriate PVDC tape around overlapped butt joint.

Continuous jacket can be spiral-wrapped around a length of pipe insulation. Apply adhesive or PVDC tape at overlapped spiral edge. When electing to use adhesives, refer to manufacturer's written instructions for application of adhesives along this spiral edge to maintain a permanent bond.

Jacket can be wrapped in cigarette fashion along length of roll for insulation systems with an outer circumference of 33-1/2 inches (850 mm) or less. The 33-1/2-inch- (850-mm-) circumference limit allows for 2-inch- (50-mm-) overlap seal. Using the length of roll allows for longer sections of jacket to be installed at one time. Use adhesive on the lap seal. Visually inspect lap seal for "fishmouthing," and use PVDC tape along lap seal to secure joint.

Repair holes or tears in PVDC jacket by placing PVDC tape over the hole or tear and wrapping a minimum of 1-1/4 circumferences to avoid damage to tape edges.

FINISHES

Coordinate first paragraph below with Section 099113 "Exterior Painting" and Section 099123 "Interior Painting." If specifying PVC jackets, consult jacket manufacturers to determine suitable paint products and revise painting Sections to suit Project.

Pipe Insulation with ASJ, Glass-Cloth, or Other Paintable Jacket Material: Paint jacket with paint system identified below and as specified in Section 099113 "Exterior Painting" and Section 099123 "Interior Painting."

Retain paint system in subparagraph below for a flat, latex-emulsion size over insulation covering an exterior that is subject to normal use and moderate environments.

Flat Acrylic Finish: [Two] <Insert number> finish coats over a primer that is compatible with jacket material and finish coat paint. Add fungicidal agent to render fabric mildew proof.

Finish Coat Material: Interior, flat, latex-emulsion size.

Flexible Elastomeric Thermal Insulation: After adhesive has fully cured, apply two coats of insulation manufacturer's recommended UV protective coating.

Color: Final color as selected by Architect. Vary first and second coats to allow visual inspection of the completed Work.

Do not field paint aluminum or stainless-steel jackets.

FIELD QUALITY CONTROL

Inspections in this article are destructive. Retain if workmanship quality is an important requirement. Architect should be prepared to reject all work if defective work is discovered in sample inspection.

Retain one of first two paragraphs below to identify who shall perform tests and inspections. If retaining second option in first paragraph, or if retaining second paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require Contractor to perform tests and inspections.

Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

Tests and Inspections:

Inspect pipe, fittings, strainers, and valves, randomly selected by Architect, by removing field-applied jacket and insulation in layers in reverse order of their installation. Extent of inspection shall be limited to [three] <Insert number> locations of straight pipe, [three] <Insert number> locations of threaded fittings, [three] <Insert number> locations of welded fittings, [two] <Insert number> locations of threaded strainers, [two] <Insert number> locations of welded strainers, [three] <Insert number> locations of threaded valves, and [three] <Insert number> locations of flanged valves for each pipe service defined in the "Piping Insulation Schedule, General" Article.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

All insulation applications will be considered defective Work if sample inspection reveals noncompliance with requirements.

Materials and thicknesses in schedules below are for single-layer applications. If multilayer applications are needed, insert additional requirements.

PIPING INSULATION SCHEDULE, GENERAL

Acceptable preformed pipe and tubular insulation materials and thicknesses are identified for each piping system and pipe size range. If more than one material is listed for a piping system, selection from materials listed is Contractor's option.

Items Not Insulated: Unless otherwise indicated, do not install insulation on the following:

Drainage piping located in crawl spaces.

Underground piping.

Chrome-plated pipes and fittings unless there is a potential for personnel injury.

Piping insulation schedules in first three articles below specify commonly used insulation materials and thicknesses by pipe size range for each service. LEED Prerequisite EA 2 requires that pipe insulation thickness comply with ASHRAE/IESNA 90.1 table titled "Minimum Pipe Insulation Thickness." Not all materials and thicknesses may be suitable for a specific project. Revise to suit Project after considering all parameters that impact selection. Do not duplicate requirements inserted in "Insulation Materials" Article. See Evaluations for more information and guidance.

Because cellular glass is brittle, the minimum thickness recommended is 1-1/2 inches (38 mm). Potential for breakage increases if thinner insulation is used.

INDOOR PIPING INSULATION SCHEDULE

See the Insulation Evaluation tables in the Evaluations for rankings of different insulation types for different service ranges.

Retain one or more options in subparagraphs below to allow Contractor to select piping materials from those retained.

Condensate and Equipment Drain Water below 60 Deg F (16 Deg C):

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert dimension> thick.

Polyolefin: [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert dimension> thick.

Chilled Water and Brine, 40 Deg F (5 Deg C) and below:

[NPS 3 (DN 80)] <Insert pipe size> and Smaller: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert dimension> thick.

Polyolefin: [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert dimension> thick.

[NPS 4 (DN 100) to NPS 12 (DN 300)] <Insert pipe size range>: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert dimension> thick.

Polyolefin: [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert dimension> thick.

[NPS 12 (DN 300)] <Insert pipe size> and Larger: Insulation shall be[ one of] the following:

Retain one or more of both subparagraphs below.

Cellular Glass: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber, [Preformed Pipe, Type I, ] [or] [Pipe and Tank Insulation, ]: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Chilled Water and Brine, above 40 Deg F (5 Deg C):

[NPS 10 (DN 250)] <Insert pipe size> and Smaller: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert dimension> thick.

Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

[NPS 12 (DN 300)] <Insert pipe size> and Larger: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Cellular Glass: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber [Preformed Pipe, Type I, ] [or] [Pipe and Tank Insulation, ]: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Condenser-water supply and return piping located indoors and operating in range of 55 to 105 deg F (13 to 41 deg C) is not always insulated. If condenser-water system operates as part of a water-side economizer cycle or if Project requires condensation control, piping should be insulated.

Condenser-Water Supply and Return:

[NPS 10 (DN 250)] <Insert pipe size> and Smaller: Insulation shall be[ one of] the following:

Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

[NPS 12 (DN 300)] <Insert pipe size> and Larger: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Cellular Glass: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber, [Preformed Pipe, Type I] [or] [Pipe and Tank Insulation]: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Heating-Hot-Water Supply and Return, 200 Deg F (93 Deg C) and Below:

[NPS 10 (DN 250)] <Insert pipe size> and Smaller: Insulation shall be[ one of] the following:

Retain one or more of first four subparagraphs below.

Flexible Elastomeric: [1 inch (25 mm)] [2 inches (50 mm)] <Insert dimension> thick.

Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

Cellular Glass: [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe, Type I: [1 inch (25 mm)] [2 inches (50 mm)] <Insert dimension> thick.

[NPS 12 (DN 300)] <Insert pipe size> and Larger: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Cellular Glass: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber, [Preformed Pipe, Type I] [or] [Pipe and Tank Insulation]: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Heating-Hot-Water Supply and Return, above 200 Deg F (93 Deg C):

[NPS 3/4 (DN 20)] <Insert pipe size> and Smaller: Insulation shall be[ one of] the following:

Retain one or more of first three subparagraphs below.

Calcium Silicate: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Cellular Glass: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe, Type I or II: [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert dimension> thick.

[NPS 1 (DN 25)] <Insert pipe size> and Larger: Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

Calcium Silicate: [3 inches (75 mm)] [4 inches (100 mm)] <Insert dimension> thick.

Cellular Glass: [3 inches (75 mm)] [4 inches (100 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe, Type I or II: [3 inches (75 mm)] [4 inches (100 mm)] <Insert dimension> thick.

Steam and Steam Condensate, 350 Deg F (177 Deg C) and Below:

[NPS 3/4 (DN 20)] <Insert pipe size> and Smaller: Insulation shall be[ one of] the following:

Retain one or more of first three subparagraphs below.

Calcium Silicate: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Cellular Glass: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe, Type I or II: [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert dimension> thick.

[NPS 1 (DN 25)] <Insert pipe size> and Larger: Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

Calcium Silicate: [3 inches (75 mm)] [4 inches (100 mm)] <Insert dimension> thick.

Cellular Glass: [3 inches (75 mm)] [4 inches (100 mm)] <Insert dimension> thick.

Mineral-Fiber, [Preformed Pipe, Type I or II] [or] [Pipe and Tank Insulation]: [3 inches (75 mm)] [4 inches (100 mm)] <Insert dimension> thick.

Steam and Steam Condensate, above 350 Deg F (177 Deg C):

[NPS 3/4 (DN 20)] <Insert pipe size> and Smaller: Insulation shall be[ one of] the following:

Retain one or more of first three subparagraphs below.

Calcium Silicate: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Cellular Glass: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe, Type I or II: [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert dimension> thick.

[NPS 1 (DN 25)] <Insert pipe size> and Larger: Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

Calcium Silicate: [3 inches (75 mm)] [4 inches (100 mm)] <Insert dimension> thick.

Cellular Glass: [3 inches (75 mm)] [4 inches (100 mm)] <Insert dimension> thick.

Mineral-Fiber, [Preformed Pipe, Type I or II] [or] [Pipe and Tank Insulation]: [3 inches (75 mm)] [4 inches (100 mm)] <Insert dimension> thick.

Refrigerant Suction and Hot-Gas Piping:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

Refrigerant Suction and Hot-Gas Flexible Tubing:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

Dual-Service Heating and Cooling, 40 to 200 Deg F (5 to 93 Deg C):

[NPS 10 (DN 250)] <Insert pipe size> and Smaller: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [1 inch (25 mm)] )] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe, Type I: [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert dimension> thick.

[NPS 12 (DN 300)] <Insert pipe size> and Larger: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Cellular Glass: [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber, [Preformed Pipe, Type I] [or] [Pipe and Tank Insulation]: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick.

Heat-Recovery Piping:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

Polyolefin: [1 inch (25 mm)] <Insert dimension> thick.

OUTDOOR, ABOVEGROUND PIPING INSULATION SCHEDULE

See the Insulation Evaluation tables in the Evaluations for rankings of different insulation types for different service ranges.

In addition to other criteria, insulate outdoor piping for freeze protection.

Chilled Water and Brine:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [3 inches (75 mm)] <Insert dimension> thick.

Polyolefin: [3 inches (75 mm)] <Insert dimension> thick.

Condenser-Water Supply and Return:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

Polyolefin: [2 inches (50 mm)] <Insert dimension> thick.

Heating-Hot-Water Supply and Return, 200 Deg F (93 Deg C) and Below:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

Cellular Glass: [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe Insulation, Type I: [2 inches (50 mm)] <Insert dimension> thick.

Heating-Hot-Water Supply and Return, above 200 Deg F (93 Deg C):

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

Calcium Silicate: [3 inches (75 mm)] <Insert dimension> thick.

Cellular Glass: [3 inches (75 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe Insulation, Type I or II: [2 inches (50 mm)] <Insert dimension> thick.

Steam and Steam Condensate, 350 Deg F (177 Deg C) and Below:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

Calcium Silicate: [4 inches (100 mm)] <Insert dimension> thick.

Cellular Glass: [4 inches (100 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe Insulation, Type I or II: [3 inches (75 mm)] <Insert dimension> thick.

Steam and Steam Condensate, above 350 Deg F (177 Deg C):

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

Calcium Silicate: [5 inches (125 mm)] <Insert dimension> thick.

Cellular Glass: [5 inches (125 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe Insulation, Type I or II: [4 inches (100 mm)] <Insert dimension> thick.

Refrigerant Suction and Hot-Gas Piping:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

Polyolefin: [2 inches (50 mm)] <Insert dimension> thick.

Refrigerant Suction and Hot-Gas Flexible Tubing:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

Polyolefin: [2 inches (50 mm)] <Insert dimension> thick.

Heat-Recovery Piping:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

Polyolefin: [2 inches (50 mm)] <Insert dimension> thick.

Dual-Service Heating and Cooling:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe Insulation, Type I: [2 inches (50 mm)] <Insert dimension> thick.

Fuel Oil Piping, Heated:

All Pipe Sizes: Insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

Cellular Glass: [2 inches (50 mm)] <Insert dimension> thick.

Mineral-Fiber, Preformed Pipe Insulation, Type I: [2 inches (50 mm)] <Insert dimension> thick.

OUTDOOR, UNDERGROUND PIPING INSULATION SCHEDULE

Insulation specified in this article is limited to those insulation types that have high compressive strength. Other insulation types may be considered acceptable and should be evaluated on a project basis. Cellular glass is best suited for applications below 250 deg F (121 deg C) because of its moisture-resistant properties.

See the Insulation Evaluation tables in the Evaluations for rankings of different insulation types for different service ranges.

Loose-fill insulation, for belowground piping, is specified in Section 232113.13 "Underground Hydronic Piping" and Section 336313 "Underground Steam and Condensate Distribution Piping."

Chilled Water, All Sizes: Cellular glass, [2 inches (50 mm)] <Insert dimension> thick.

Condenser-Water Supply and Return, All Sizes: Cellular glass, [2 inches (50 mm)] <Insert dimension> thick.

Heating-Hot-Water Supply and Return, All Sizes, 200 Deg F (93 Deg C) and Below: Cellular glass, [3 inches (75 mm)] <Insert dimension> thick.

Heating-Hot-Water Supply and Return, All Sizes, above 200 Deg F (93 Deg C):

Retain one or both subparagraphs below.

Calcium Silicate: [3 inches (75 mm)] <Insert dimension> thick.

Cellular Glass: [3 inches (75 mm)] <Insert dimension> thick.

Steam and Steam Condensate, All Sizes, 350 Deg F (177 Deg C) and Below:

Retain one or both subparagraphs below.

Calcium Silicate: [4 inches (100 mm)] <Insert dimension> thick.

Cellular Glass: [4 inches (100 mm)] <Insert dimension> thick.

Steam and Steam Condensate, All Sizes, above 350 Deg F (177 Deg C):

Retain one or both subparagraphs below.

Calcium Silicate: [5 inches (125 mm)] <Insert dimension> thick.

Cellular Glass: [5 inches (125 mm)] <Insert dimension> thick.

Dual-Service Heating and Cooling, All Sizes, 40 to 200 Deg F (4 to 93 Deg C): Cellular glass, [3 inches (75 mm)] <Insert dimension> thick.

Fuel Oil Piping, All Sizes, Heated: Cellular glass, [2 inches (50 mm)] <Insert dimension> thick.

INDOOR, FIELD-APPLIED JACKET SCHEDULE

Possible variations of jackets by location are endless. This article specifies locations in two broad categories: concealed and exposed. Revise if additional delineation is necessary.

Install jacket over insulation material. For insulation with factory-applied jacket, install the field-applied jacket over the factory-applied jacket.

If more than one material is listed, selection from materials listed is Contractor's option.

Piping, Concealed:

Retain one of six subparagraphs below.

None.

[PVC] [PVC, Color-Coded by System]: [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

<Insert jacket type>.

Piping, Exposed:

Retain one of six subparagraphs below.

None.

[PVC] [PVC, Color-Coded by System]: [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

<Insert jacket type>.

OUTDOOR, FIELD-APPLIED JACKET SCHEDULE

Possible variations of jackets by location are endless. This article specifies locations in two broad categories: concealed and exposed. Revise if additional delineation is necessary.

30-mil (0.8-mm) or heavier PVC is recommended for outdoor applications. 40-mil (1.0-mm) PVC does not meet a flame-spread index of 25 and a smoke-developed index of 50; however, a flame-spread or smoke-developed index is not a requirement for outdoor applications.

0.024-inch (0.61-mm) or heavier aluminum is recommended for outdoor applications.

Painted aluminum increases surface emissivity and provides added chemical resistance. See Evaluations for discussion of emissivity.

0.016-inch (0.41-mm) or heavier stainless steel is recommended for outdoor applications.

Z-shaped locking seam is recommended for metal jackets located in unprotected applications that are exposed to severe weather.

Install jacket over insulation material. For insulation with factory-applied jacket, install the field-applied jacket over the factory-applied jacket.

If more than one material is listed, selection from materials listed is Contractor's option.

Piping, Concealed:

Retain one of six subparagraphs below.

None.

[PVC] [PVC, Color-Coded by System]: [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

<Insert jacket type>.

Piping, Exposed:

Retain one of four subparagraphs below.

PVC: [20 mils (0.5 mm)] [30 mils (0.8 mm)] [40 mils (1.0 mm)] thick.

[Painted ]Aluminum, [Smooth] [Corrugated] [Stucco Embossed] [with Z-Shaped Locking Seam]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed] [with Z-Shaped Locking Seam]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

<Insert jacket type>.

UNDERGROUND, FIELD-INSTALLED INSULATION JACKET

For underground direct-buried piping applications, install underground direct-buried jacket over insulation material.

END OF SECTION 230719